## Inverter status_New
Planta | Falta | Bit | Mensagem
Pirapora | Fault1 | B0 | ECAT operation fault
Pirapora | Fault1 | B1 | FPGA version wrong
Pirapora | Fault1 | B2 | PIB watchdog fault
Pirapora | Fault1 | B3 | DC-Link overvoltage
Pirapora | Fault1 | B4 | Float controller fault
Pirapora | Fault1 | B5 | DC-Link short circuit
Pirapora | Fault1 | B6 | Pole grounding
Pirapora | Fault1 | B7 | Not used
Pirapora | Fault1 | B8 | IGBT VCE desaturation fault
Pirapora | Fault1 | B9 | Not used
Pirapora | Fault1 | B10 | IGBT feedback fault
Pirapora | Fault1 | B11 | Not used
Pirapora | Fault1 | B12 | Not used
Pirapora | Fault1 | B13 | Not used
Pirapora | Fault1 | B14 | Not used
Pirapora | Fault1 | B15 | Not used
Pirapora | Fault2 | B0 | PIB internal power supply
Pirapora | Fault2 | B1 | PIB measurement connector
Pirapora | Fault2 | B2 | Not used
Pirapora | Fault2 | B3 | PIB amplifier connection
Pirapora | Fault2 | B4 | PIB terminal supply
Pirapora | Fault2 | B5 | Current clipping timeout
Pirapora | Fault2 | B6 | Short circuit
Pirapora | Fault2 | B7 | Not used
Pirapora | Fault2 | B8 | Heat sink over-temperature
Pirapora | Fault2 | B9 | 24V terminal supply short circuit
Pirapora | Fault2 | B10 | Fieldbus connection fault
Pirapora | Fault2 | B11 | Battery synchronisation fault
Pirapora | Fault2 | B12 | Short-Circuit-To-Earth
Pirapora | Fault2 | B13 | DC-link under-voltage
Pirapora | Fault2 | B14 | Not used
Pirapora | Fault2 | B15 | Not used
Pirapora | Fault3 | B0 | Line voltage fault
Pirapora | Fault3 | B1 | Line voltage measurement
Pirapora | Fault3 | B2 | AC-Circuit breaker tripped
Pirapora | Fault3 | B3 | Feedback AC circuit breaker
Pirapora | Fault3 | B4 | Precharging failed
Pirapora | Fault3 | B5 | Line filter
Pirapora | Fault3 | B6 | Feedback discharging contactor
Pirapora | Fault3 | B7 | Feedback DC circuit breaker
Pirapora | Fault3 | B8 | Amplifier board contactor
Pirapora | Fault3 | B9 | DC current direction fault (reverse Idc)
Pirapora | Fault3 | B10 | UPS fault
Pirapora | Fault3 | B11 | Feedback PV short circuit breaker
Pirapora | Fault3 | B12 | Not used
Pirapora | Fault3 | B13 | Not used
Pirapora | Fault3 | B14 | Not used
Pirapora | Fault3 | B15 | Not used
Pirapora | Fault4 | B0 | Heat sink temperature measurement
Pirapora | Fault4 | B1 | Heat sink under-temperature
Pirapora | Fault4 | B2 | External fan
Pirapora | Fault4 | B3 | Power electronics cubicle fan
Pirapora | Fault4 | B4 | Line inductor fan
Pirapora | Fault4 | B5 | Cooling water over-temperature
Pirapora | Fault4 | B6 | Cooling water pressure fault
Pirapora | Fault4 | B7 | Cooling water pump fault
Pirapora | Fault4 | B8 | Water heating/cooling fault
Pirapora | Fault4 | B9 | Power electronics cubicle over-temperature
Pirapora | Fault4 | B10 | Line inductor cubicle over-temperature
Pirapora | Fault4 | B11 | MV Transformer fault
Pirapora | Fault4 | B12 | Isolation fault
Pirapora | Fault4 | B13 | Not used
Pirapora | Fault4 | B14 | Auxiliary supply fault
Pirapora | Fault4 | B15 | Fluid cooling system fault
Pirapora | Warning1 | B0 | Heat sink over-temperature
Pirapora | Warning1 | B1 | Earth current
Pirapora | Warning1 | B2 | Line under voltage
Pirapora | Warning1 | B3 | Cooling water over-temperature
Pirapora | Warning1 | B4 | Cooling water pressure
Pirapora | Warning1 | B5 | Water pressure sensor
Pirapora | Warning1 | B6 | Water heating
Pirapora | Warning1 | B7 | Fuse discharging resistor
Pirapora | Warning1 | B8 | Cubicle heater
Pirapora | Warning1 | B9 | Power electronics cubicle over-temperature
Pirapora | Warning1 | B10 | Line inductor over-temperature
Pirapora | Warning1 | B11 | Not used
Pirapora | Warning1 | B12 | Switching cycle AC-Breaker (daily)
Pirapora | Warning1 | B13 | Pole grounding
Pirapora | Warning1 | B14 | Contactor pole grounding
Pirapora | Warning1 | B15 | Transformer over-temperature
Pirapora | Warning2 | B0 | CPU board over-temperature
Pirapora | Warning2 | B1 | CPU core over-temperature
Pirapora | Warning2 | B2 | Unbalanced DC-Link
Pirapora | Warning2 | B3 | Fan lifetime exceeded
Pirapora | Warning2 | B4 | dc-link voltage oscillation
Pirapora | Warning2 | B5 | Water inlet temperature sensor
Pirapora | Warning2 | B6 | Outside temperature sensor
Pirapora | Warning2 | B7 | Line inductor temperature sensor
Pirapora | Warning2 | B8 | Power electronics cubicle temperature sensor
Pirapora | Warning2 | B9 | Shut down with local/remote changeover
Pirapora | Warning2 | B10 | Disconnection from PV generator
Pirapora | Warning2 | B11 | Inaccurate power measurement for MPPT
Pirapora | Warning2 | B12 | External fan
Pirapora | Warning2 | B13 | Fieldbus warning
Pirapora | Warning2 | B14 | AC Breaker switching cycle exceeded
Pirapora | Warning2 | B15 | DC Breaker switching cycle exceeded
Pirapora | Warning3 | B0 | Isolation warning
Pirapora | Warning3 | B1 | Float controller warning
Pirapora | Warning3 | B2 | Over voltage protection
Pirapora | Warning3 | B3 | Not used
Pirapora | Warning3 | B4 | Not used
Pirapora | Warning3 | B5 | Not used
Pirapora | Warning3 | B6 | Not used
Pirapora | Warning3 | B7 | Not used
Pirapora | Warning3 | B8 | Not used
Pirapora | Warning3 | B9 | Not used
Pirapora | Warning3 | B10 | Not used
Pirapora | Warning3 | B11 | Not used
Pirapora | Warning3 | B12 | Not used
Pirapora | Warning3 | B13 | Not used
Pirapora | Warning3 | B14 | Not used
Pirapora | Warning3 | B15 | Not used
Pirapora | Status1 | B0 | Ready to switch ON
Pirapora | Status1 | B1 | Switched ON (power ok)
Pirapora | Status1 | B2 | Operation enabled (RUN)
Pirapora | Status1 | B3 | Fault present
Pirapora | Status1 | B4 | Voltage enabled (drive released)
Pirapora | Status1 | B5 | Quick stop active
Pirapora | Status1 | B6 | Switching ON disabled
Pirapora | Status1 | B7 | Warning present
Pirapora | Status1 | B8 | Line loss
Pirapora | Status1 | B9 | Remote
Pirapora | Status1 | B10 | DC circuit breaker ON
Pirapora | Status1 | B11 | Internal limit active
Pirapora | Status1 | B12 | FRT
Pirapora | Status1 | B13 | Converter test mode
Pirapora | Status1 | B14 | Internal alive toggle
Pirapora | Status1 | B15 | Bus alive toggle
Pirapora | Status2 | B0 | B0 Manual stop
Pirapora | Status2 | B1 | B1 Automatic mode
Pirapora | Status2 | B2 | Waiting
Pirapora | Status2 | B3 | Cooling initialization
Pirapora | Status2 | B4 | PV-mode
Pirapora | Status2 | B5 | MPP search
Pirapora | Status2 | B6 | MPP reached
Pirapora | Status2 | B7 | PV Power reduction
Pirapora | Status2 | B8 | VAR at night mode
Pirapora | Status2 | B9 | ECAT operational
Pirapora | Status2 | B10 | Buttery operating mode
Pirapora | Status2 | B11 | Synchronization achieved
Pirapora | Status2 | B12 | Not used
Pirapora | Status2 | B13 | Not used
Pirapora | Status2 | B14 | Not used
Pirapora | Status2 | B15 | Emergency OFF
GUI | Fault1 | B0 | ECAT fault
GUI | Fault1 | B1 | FPGA version
GUI | Fault1 | B2 | PIB Watchdog
GUI | Fault1 | B3 | DC-Link overvoltage
GUI | Fault1 | B4 | Flaat controller
GUI | Fault1 | B5 | DC-Link short circuit
GUI | Fault1 | B6 | Pole grounding
GUI | Fault1 | B7 | not used
GUI | Fault1 | B8 | IGBT desaturation
GUI | Fault1 | B9 | not used
GUI | Fault1 | B10 | IGBT Feedback
GUI | Fault1 | B11 | not used
GUI | Fault1 | B12 | not used
GUI | Fault1 | B13 | PIB Central fault
GUI | Fault1 | B14 | not used
GUI | Fault1 | B15 | not used
GUI | Fault2 | B0 | PIB internal Power Supply
GUI | Fault2 | B1 | Short Firing
GUI | Fault2 | B2 | not used
GUI | Fault2 | B3 | Amplifier Connector
GUI | Fault2 | B4 | not used
GUI | Fault2 | B5 | Current Clipping Timeout
GUI | Fault2 | B6 | Short Circuit
GUI | Fault2 | B7 | not used
GUI | Fault2 | B8 | Heat Sink Over temperature
GUI | Fault2 | B9 | terminal Supply 24V
GUI | Fault2 | B10 | Fieldbus fault
GUI | Fault2 | B11 | Battery Synchronisation Fault
GUI | Fault2 | B12 | Earth Fault
GUI | Fault2 | B13 | DC-Link Under Voltage
GUI | Fault2 | B14 | not used
GUI | Fault2 | B15 | not used
GUI | Fault3 | B0 | Line voltage
GUI | Fault3 | B1 | Line voltage measurement
GUI | Fault3 | B2 | AC circuit breaker
GUI | Fault3 | B3 | FB AC circuit breaker
GUI | Fault3 | B4 | Pre-charging failed
GUI | Fault3 | B5 | Line filter
GUI | Fault3 | B6 | Discharging failed
GUI | Fault3 | B7 | Feedback DC circuit breaker
GUI | Fault3 | B8 | Amplifier board contactor
GUI | Fault3 | B9 | DC current direction
GUI | Fault3 | B10 | UPS
GUI | Fault3 | B11 | FB PV short circuit breaker
GUI | Fault3 | B12 | Isolation fault
GUI | Fault3 | B13 | Max Output Frequency
GUI | Fault3 | B14 | FPGA Firing
GUI | Fault3 | B15 | PIB hardware configuration
GUI | Fault4 | B0 | Heat Sink temperature measurement
GUI | Fault4 | B1 | Low heat Sink temperature
GUI | Fault4 | B2 | External fan
GUI | Fault4 | B3 | Cubicle fan
GUI | Fault4 | B4 | Auxiliary supply
GUI | Fault4 | B5 | Water over temperature
GUI | Fault4 | B6 | Water pressure
GUI | Fault4 | B7 | Water pump
GUI | Fault4 | B8 | initial water heating, initial cooling
GUI | Fault4 | B9 | Cubicle over temperature
GUI | Fault4 | B10 | Line inductor over temperature
GUI | Fault4 | B11 | MV transformer vacuum
GUI | Fault4 | B12 | MV transformer pressure
GUI | Fault4 | B13 | Mv transformer oil level
GUI | Fault4 | B14 | MV transformer temperature
GUI | Fault4 | B15 | FCS
GUI | Warning1 | B0 | Heat Sink over temperature
GUI | Warning1 | B1 | Earth fault
GUI | Warning1 | B2 | Line under voltage
GUI | Warning1 | B3 | Water over temperature
GUI | Warning1 | B4 | Water pressure
GUI | Warning1 | B5 | Water pressure sensor
GUI | Warning1 | B6 | Water heating
GUI | Warning1 | B7 | Fuse discharging resistor
GUI | Warning1 | B8 | Cubicle heater
GUI | Warning1 | B9 | PE cubicle over temperature
GUI | Warning1 | B10 | Line inductor over temperature
GUI | Warning1 | B11 | not used
GUI | Warning1 | B12 | Pole grounding over current level 1
GUI | Warning1 | B13 | Pole grounding over current level 2
GUI | Warning1 | B14 | Pole grounding Feedback contactor
GUI | Warning1 | B15 | Pole grounding fuse
GUI | Warning2 | B0 | CPU board over temperature
GUI | Warning2 | B1 | CPU core over temperature
GUI | Warning2 | B2 | Unbalanced dc-link voltage
GUI | Warning2 | B3 | Fan life time exceeded
GUI | Warning2 | B4 | dc-link voltage ocillation
GUI | Warning2 | B5 | Water temperature sensor
GUI | Warning2 | B6 | Outside temperature sensor
GUI | Warning2 | B7 | Line inductor temperature sensor
GUI | Warning2 | B8 | PE cubicle temperature sensor
GUI | Warning2 | B9 | Shut down with Local/Remote change-over
GUI | Warning2 | B10 | Disconnection from PV genertion
GUI | Warning2 | B11 | inaccurate power measurement for MPPT
GUI | Warning2 | B12 | External fan*
GUI | Warning2 | B13 | Switching cycle AC circuit breaker
GUI | Warning2 | B14 | AC breaker life time exceeded
GUI | Warning2 | B15 | DC breaker life time exceeded
GUI | Warning3 | B0 | Isolation warning
GUI | Warning3 | B1 | Float controller
GUI | Warning3 | B2 | Over voltage protection
GUI | Warning3 | B3 | not used
GUI | Warning3 | B4 | not used
GUI | Warning3 | B5 | Filter cubicle fan
GUI | Warning3 | B6 | not used
GUI | Warning3 | B7 | Cubicle temperature warning
GUI | Warning3 | B8 | SRAM Backup Failure
GUI | Warning3 | B9 | Fieldbus warning
GUI | Warning3 | B10 | MV transformer over temperature
GUI | Warning3 | B11 | Isolation sensor
GUI | Warning3 | B12 | CPU Synchronization
GUI | Warning3 | B13 | External Power reference
GUI | Warning3 | B14 | not used
GUI | Warning3 | B15 | not used
GUI | Status1 | B0 | Ready to switch ON
GUI | Status1 | B1 | Switched ON (power ok)
GUI | Status1 | B2 | Operation enbled (RUN)
GUI | Status1 | B3 | Faul present
GUI | Status1 | B4 | Voltage enabled (drive released)
GUI | Status1 | B5 | Quick stop active
GUI | Status1 | B6 | Swiitching ON disabled
GUI | Status1 | B7 | Warning present
GUI | Status1 | B8 | Line loss
GUI | Status1 | B9 | Remote
GUI | Status1 | B10 | DC circuit breaker ON
GUI | Status1 | B11 | Internal limit active
GUI | Status1 | B12 | FRT
GUI | Status1 | B13 | Converter test mode
GUI | Status1 | B14 | Internal alive toggle
GUI | Status1 | B15 | Bus alive toggle
GUI | Status2 | B0 | Manual stop
GUI | Status2 | B1 | Automatic mode
GUI | Status2 | B2 | Waiting
GUI | Status2 | B3 | Cooling initialization
GUI | Status2 | B4 | PV-mode
GUI | Status2 | B5 | MPP search
GUI | Status2 | B6 | MPP reached
GUI | Status2 | B7 | PV Power reduction
GUI | Status2 | B8 | VAR at night mode
GUI | Status2 | B9 | ECAT operational
GUI | Status2 | B10 | Battery operating mode
GUI | Status2 | B11 | Synchronization achieved
GUI | Status2 | B12 | not used
GUI | Status2 | B13 | not used
GUI | Status2 | B14 | Isolation monitoring procedure
GUI | Status2 | B15 | Hard trip
GUI | Status3 | B0 | DC Circuit Breaker Test